Procurement and Installation of HDPE DN 400 mm Pipeline for 504 Meters: Butt Fusion Jointing and Hydrotesting at 7.5 Bar fo 24 Hours

Mohammad Zaki Budiman, S.T.,M.T.1 and Ir. Benny Dwika Lonanda, M.T, IPM, ASEAN Eng2

1PT. Cahaya Adiwangsa Teta, Director, Padang, Sumatera Barat

Email: zakibudiman.mt@gmail.com

2Program Studi Program Profesi Insinyur Pascasarjana Universitas Andalas

Email: bdleonanda@gmail.com

### ABSTRACT

This project involves the procurement and installation of a 504-meter HDPE DN 400 mm pipeline to support clean water distribution in Padang city area. Butt fusion was used for jointing, while hydrotesting at 7.5 bar pressure for 24 hours ensured system integrity. Material procurement required a months, followed by a 4-month installation period, making the total project duration 5 months. Challenges due to the rainy season included water pooling and schedule adjustments. The total project cost of 2 billion IDR covered material procurement, labor, and mitigation efforts for weather-related obstacles. The project was successfully completed with high efficiency and compliance with technical standards.

#### Keyword: HDPE pipe, clean water distribution, pipe installation, butt fusion, hydrostatic pressure test.

### 1. Introduction

#### 1.1 Background

Reliable access to clean water is essential for public health and economic development. Modern pipeline systems must meet stringent quality and durability standards to ensure the uninterrupted delivery of water. High-Density Polyethylene (HDPE) DN 400 mm pipes were chosen for this project due to their excellent properties, including durability, flexibility, and resistance to corrosion.

#### 1.2 Objectives

This paper aims to document the processes involved in the procurement, installation, and testing of a clean water pipeline system in Padang, emphasizing the use of HDPE pipes, butt fusion jointing, and hydrotesting.

#### 1.3 Significance

The adoption of HDPE pipes and advanced jointing techniques such as butt fusion underscores a commitment to reliable, efficient, and cost-effective water distribution solutions.

2. Literature Review

2.1 HDPE Pipes in Water Distribution Systems

High-Density Polyethylene (HDPE) pipes are widely used in water distribution due to their high durability, corrosion resistance, and flexibility. Studies such as those by Riffat and Ma (2019) have highlighted HDPE's sustainable characteristics, making it suitable for long-term infrastructure projects. According to the Indonesian National Standard (SNI 4829:2015), HDPE pipes meet stringent technical requirements for clean water distribution.

2.2 Butt Fusion Jointing Technique

The butt fusion technique is recognized as an effective method for joining HDPE pipes. Research by Beier and Goforth (2021) emphasizes that fusion jointing provides leak-proof and durable connections when performed under controlled conditions. ASTM F2620 standards outline the proper procedures for heat fusion joining, ensuring consistency and reliability.

2.3 Hydrotesting for Pipeline Integrity

Hydrostatic pressure testing is a critical procedure to verify the structural integrity of pipelines. Silva and da Silva (2019) demonstrated that hydrotesting effectively identifies potential leaks or deformations in HDPE pipes under operational pressures. This technique ensures compliance with ISO 4427-2:2019 standards, confirming a pipeline's readiness for service.

2.4 Challenges in Pipeline Installation

Environmental factors, such as heavy rainfall, can significantly impact pipeline installation schedules. Choi et al. (2020) examined the effects of weather conditions on HDPE pipe installation in tropical regions, suggesting that proactive water management strategies and flexible scheduling are essential for mitigating delays.

### 3. Methods

#### 3.1. Material Procurement

- Procurement Duration:

  - The procurement process, including ordering, production, and material transportation, took 2 months.

  - Key challenges included transportation delays due to adverse weather conditions.

- Materials Provided:

  - HDPE DN 400 mm pipe, PN 10, SDR 17.

  - Butt fusion machine and auxiliary tools.

- Project Budget Allocation:

  - Material procurement: 60%.

  - Labor and operational costs: 30%.

  - Weather-related mitigation: 10%.

#### 3.2. Pipeline Installation

- Site Preparation:

  - Trenches were excavated with an average depth of 1.5 meters.

  - Water pooling caused by heavy rainfall was managed using water pumps.

- Butt Fusion Method:

  - Pipe ends were cleaned and leveled using a facing tool.

  - The pipes were heated at 210–220°C until a molten layer formed.

  - Jointing was performed under constant pressure, followed by cooling for 10–15 minutes.

- Hydrotesting:

  - The pipeline system was filled with water and tested at 7.5 bar for 24 hours.

  - Parameters tested included leaks, pressure stability, and pipe deformation.

### 4. Results and Discussion

- Material Procurement:

  - Material procurement was completed within 2 months.

  - Transportation delays were minimal and resolved promptly.

- Pipeline Installation:

  - A total of 20 butt fusion joints were successfully completed without defects.

  - Installation was completed in 4 months, with a 10–20% slowdown in certain segments due to heavy rainfall.

- Hydrotesting Results:

  - The pipeline maintained 7.5 bar pressure for 24 hours without significant pressure drops.

  - The system was confirmed leak-free and operationally ready.

- Cost and Efficiency:

  - The project was completed with a total cost of 2 billion IDR, covering material procurement, labor, and weather-related adjustments.

  - Despite challenges, the project was finished on schedule with high efficiency.

### 5. Conclusion

Material procurement for this project required 2 months, followed by a 4-month installation period, resulting in a total project duration of 6 months. Butt fusion jointing produced leak-proof connections that met technical standards, while hydrotesting at 7.5 bar for 24 hours ensured pipeline integrity. Challenges from the rainy season were mitigated using water pumps and flexible scheduling. With a total budget of 2 billion IDR, this project was completed successfully, demonstrating that proper planning can overcome technical and weather-related obstacles.

### References

- SNI 4829:2015. Pipeline Systems for Clean Water Distribution.

- ASTM F2620: Standard Practice for Heat Fusion Joining of Polyethylene Pipe.

- HDPE Technical Manual. PT XYZ.

### Bibliography

- Indonesian National Standard (SNI 4829:2015). Pipeline Systems for Clean Water Distribution. Jakarta: National Standardization Agency of Indonesia (BSN), 2015.

- ASTM F2620-13. Standard Practice for Heat Fusion Joining of Polyethylene Pipe and Fittings. West Conshohocken, PA: ASTM International, 2013.

- PT XYZ. HDPE Pipe Technical Manual. Jakarta: PT XYZ Publications, 2020.

- PPI (Plastics Pipe Institute). Handbook of Polyethylene Pipe. 2nd Edition. Irving, TX: Plastics Pipe Institute, 2016.

- International Organization for Standardization (ISO 4427-2:2019). Plastics Piping Systems – Polyethylene (PE) Pipes and Fittings for Water Supply – Part 2: Pipes. Geneva: ISO, 2019.

- Chao, Kang, et al. Engineering Applications of High-Density Polyethylene (HDPE) Pipes. Journal of Polymer Engineering, Vol. 37, No. 4, 2020, pp. 345-358.

- Beier, M., & Goforth, M. The Effect of Fusion Jointing on the Mechanical Properties of Polyethylene Piping Systems. Journal of Plastic Engineering, Vol. 31, No. 2, 2021, pp. 229-243.

- Riffat, S. B., & Ma, Z. A Review of Sustainable Water Distribution Piping Systems. Building and Environment Journal, Vol. 67, 2019, pp. 121-131.

- American Water Works Association (AWWA). Polyethylene Piping Systems for Water Distribution and Sewerage. Denver, CO: AWWA, 2018.

- Peck, D. L. The Strength of Polyethylene Pipes Under Hydrostatic Pressure. Journal of Water Distribution and Pipe Systems, Vol. 53, No. 6, 2018, pp. 1023-1034.

- Choi, S., Kim, S., & Hwang, H. Study on the Performance of HDPE Pipes for Clean Water Supply in Rainy Regions. Journal of Environmental Engineering & Science, Vol. 29, 2020, pp. 455-467.

- Wang, X., Li, Z., & Zhang, S. Analysis of Leakage Rates in Polyethylene Piping Systems under Varying Pressure Conditions. International Journal of Civil Engineering & Technology, Vol. 11, No. 8, 2020, pp. 110-119.

- Freeman, R. C., & O'Brien, L. Impact of Temperature on the Strength of Butt-Fusion Welds in HDPE Pipes. Polymer Engineering & Science, Vol. 42, No. 9, 2022, pp. 1999-2008.

- Moser, J. W., & Hill, R. M. Pipe Materials for Water Distribution Systems in Tropical and Temperate Climates. Journal of Water Resources Research, Vol. 59, No. 1, 2021, pp. 75-82.

- Silva, R. B., and da Silva, L. F. Assessment of HDPE Pipe Integrity Using Acoustic Emission during Hydrostatic Pressure Testing. Journal of Non-Destructive Testing, Vol. 25, No. 3, 2019, pp. 40-50.